## Test Results
Test Step | Description | Result | Failure Reason
Address Space Model | Defines ConformanceUnits for various features of the OPC UA AddressSpace. | FAILED | No ReadOnly NodeId defined. Please check setting '/Server Test/NodeIds/SecurityAccess/AccessLevel_CurrentRead_NotCurrentWrite'.
Address Space Atomicity | Support setting the NonatomicRead and NonatomicWrite flags in the AccessLevelEx Attribute for Variable Nodes to indicate whether Read or Write operations can be performed in atomic manner. If the flags are set to '1', atomicity cannot be assured. | FAILED | No node found that have the NonatomicRead or NonatomicWrite flag in the AccessLevelEx attribute set. Skipping Conformance Unit.
AccessLevelEx_AtomicityFlags_Check.js | Atomicity flags in the AccessLevelEx are used. | FAILED | No node found that have the NonatomicRead or NonatomicWrite flag in the AccessLevelEx attribute set. Skipping Conformance Unit.
Address Space Base | Support the NodeClasses with their Attributes and behaviour as defined in OPC UA Part 3. This includes for instance: Object, Object Type, Variable, Variable Type, References and Data Type | PASSED
BaseNodeClassComplianceCheck.js | Walks through the address space checking each Node contains the mandatory attributes, references and properties. Number of nodes checked is defined by a constant at the top of the script. | PASSED
TypeSystemStructureValidation.js | Root node has Objects, Types, and Views | PASSED
Address Space Complex Datatypes | Support ComplexData with Data Dictionary. | FAILED | Not Implemented
Address Space Events |  | FAILED | Not Implemented
Address Space Method | Support Method Nodes. | PASSED
Address Space User Level Security Base | Implements User Level access masks for base nodes, this include at least two user access masks. | FAILED | Not Implemented
Address Space UserWriteAccess | Supports UserWriteMask indicating the write access availability for all attributes for the given user, including not supported attributes. Support includes at least two levels of users. | FAILED | No ReadOnly NodeId defined. Please check setting '/Server Test/NodeIds/SecurityAccess/AccessLevel_CurrentRead_NotCurrentWrite'.
WriteToAccessLevel_CurrentWrite.js | Write: Write to a node where UserAccessLevel = CurrentWrite. | PASSED
InvalidWrite_ReadOnlyAccess.js | Write: to read-only node, based on (optional) WriteMask attribute. | FAILED | No ReadOnly NodeId defined. Please check setting '/Server Test/NodeIds/SecurityAccess/AccessLevel_CurrentRead_NotCurrentWrite'.
WriteToWritableAttributes.js | Write: to all attributes EXCEPT 'Value'; request valid encoding. | FAILED | Write. Response. ResponseHeader.
WriteDeniedByUserAccessLevel.js | Write: to a node whose UserAccessLevel != Write. Expects Bad_NotWritable. | FAILED | No writalbe node defined that is NOT writable to the current user. Please check setting '/Server Test/NodeIds/SecurityAccess/AccessLevel_CurrentWrite_NotUser'.
UserReadAccess.js |  | PASSED
AccessLevelRead.js |  | PASSED
Address Space UserWriteMask Multilevel | Supports UserWriteMask indicating the write access availability for all attributes for the given user, including not supported attributes. This includes supporting multiple levels of access control for all nodes in the system. | FAILED | Not Implemented
WriteAllWritableAttributesBasedOnWriteMask.js | Write: Write to all writable attributes of a Node, using the writeMask as a guideline. [WriteAccessMask enum currently not match Part 3 Table 3 Definition] | FAILED | The number of results does not match the number of NodesToWriteService.
WriteValidValuesToWritableAttributesBasedOnWriteMask.js | Write: Write to Value and Display name for valid, unknown, and invalid nodeIds. | FAILED | Write. Response. ResponseHeader.
WriteToInvalidNodesMultipleAttributes.js | Write: to Value and DisplayName, all NodeIds have invalid syntax. | FAILED | Write. Response. ResponseHeader.
Attribute Services | Includes ConformanceUnits to Read or Write current or historical Attribute values. | FAILED | Nodes of type Structure must be set for this test to run.
Read_Request_Default_Binary_Encoding.js | Read: Request "default binary" encoding. | FAILED | Nodes of type Structure must be set for this test to run.
Read_Request_DataEncoding_Of_Xml.js | Read: Request DataEncoding of Xml. | FAILED | Nodes of type Structure must be set for this test to run.
Read_Request_Unknown_Encoding_For_Node.js | Read: Request unknown encoding for a node. | FAILED | Needs a complex type
Read_Request_Encoding_For_Non_Value_Attribute_Of_Variable.js | Read: Request encoding for non-Value attribute of a variable. | PASSED
CreateMonitoredItems_Request_Unsupported_DataEncoding_Modbus.js | CreateMonitoredItems: Request unsupported DataEncoding, e.g. "modbus". | FAILED | Expected: BadDataEncodingUnsupported, but received: BadDataEncodingInvalid (0x80380000)
CreateMonitoredItems_DataEncoding_Namespace_Does_Not_Exist.js | CreateMonitoredItems: DataEncoding namespace does not exist. | WARNING
CreateMonitoredItems_Request_Encoding_For_Non_Value_Attribute.js | CreateMonitoredItems: Request encoding for non-Value attribute. | PASSED
ReadSingleScalarNodeValueWithServerTimestamp.js | Read: VALUE attribute of a single node. | PASSED
ReadMultipleAttributesFromValidNode.js | Read: Multiple attributes from a single node, in a single call. | PASSED
readAllAttributesFromVariableNode.js | Read all available attributes from a single (valid) node, in a single call. | PASSED
readMultipleAttributesWithMaxAgeZero.js | Read multiple attributes from a valid node with maxAge = 0. | PASSED
readDataValueWithBothTimestamps.js | Read a data value with TimestampsToReturn = BOTH | FAILED | Read. Response. Results (count: 10) with RequestHandle=9 StatusCodes check: [0] (Setting: '/Server Test/NodeIds/Static/All Profiles/Scalar/Bool') StatusCode is Good (0x00000000), .
readDataValueWithSourceTimestampOnly.js | Read a data value with timestampsToReturn = SOURCE. Lab: verify the source timestamp is returned. | PASSED
readDataValueWithServerTimestampOnly.js | Read a data value with timestampsToReturn = SERVER. Lab: verify the Server’s timestamp is returned. | PASSED
readDataValueWithNoTimestamps.js | Read a data value with timestampsToReturn = NEITHER | PASSED
readBrowseNameAttribute.js | Read: BrowseName attribute from a valid node. | PASSED
ReadAllMandatoryAttributes_MultipleNodeTypes.js | Read all available attributes from multiple valid nodes of each different node type, in a single call. | PASSED
ReadSameAttributeMultipleTimes_SingleNode.js | Read: Same attribute from same node multiple times. | PASSED
ReadEachSupportedScalarDataType.js | Read: Data-type reads. | FAILED | Read. Response. Results (count: 10) with RequestHandle=17 StatusCodes check: [0] (Setting: '/Server Test/NodeIds/Static/All Profiles/Scalar/Bool') StatusCode is Good (0x00000000), .
Read_MaxAge_Exceeds_Int32_With_Both_Timestamps.js | Read: MaxAge > Int32 | PASSED
Read_SingleNode_SequentialAttributes_NoSourceTimestamp.js | Read: Read a single attribute that is not 'Value'. Cycle through AccessLevel, BrowseName, DataType, DisplayName, Historizing, NodeClass, NodeId, UserAccessLevel, ValueRank INDIVIDUALLY. | PASSED
Read_ServerState_ExpectRunning.js | Read: Read ServerStatus.State and verify == RUNNING_0. | PASSED
ReadSingleElementFromArrayByIndexRange_ValidateAgainstFullArrayRead.js | Read: Arrays, read one node of each data type specifying an IndexRange retrieving 2nd element only. | FAILED | Read. Response.
ReadArraySubrange_IndexRange2to4_CompareWithFullArray.js | Read: Arrays of various data types from multiple Nodes (in a single call) using IndexRange 2-4. | FAILED | Read. Response.
ReadArray_Last3Elements_IndexRange.js | Read: Arrays of various data types from multiple Nodes (in a single call) using IndexRange 'last 3 items'. | FAILED | Read. Response.
ReadEventNotifierAttribute.js | Read: The EventNotifier attribute. Expects Good orBad_AttributeIdInvalid. | PASSED
ReadNonValueAttributesWithTimestampCheck.js | Read attributes (not Value); sourceTimestamp=null; serverTimestamp is valid. | PASSED
ReadMultiDimensionalArrayValueAttribute.js | Read the Value attribute of a single Node where the Value attribute is of a different data-type and is an multi dimensional array. | FAILED | No MultiDimensionalArray items configured. Please check settings.
ReadMultiDimensionalArrayValues_DifferentDataTypes.js | Read the Value attribute of multiple nodes, each Node`s Value attribute is of a different data-type and is a multi-dimensionsal array. | FAILED | No MultiDimensionalArray items configured. Please check settings.
AttributeRead_MultiDimArray_SingleElement.js | Use of IndexRange for reading a single element of a multi-dimensional array, in this case the 2nd element of the 2nd dimension. | FAILED | No MultiDimensionalArray items configured. Please check settings.
ReadRange_MultiDimArray_2To4_SecondDimension.js | Use of IndexRange for reading a range of indexes of a multi-dimentional array, in this case a range is from 2-4 in the second dimension. | FAILED | No MultiDimensionalArray items configured. Please check settings.
ReadRange_Last3_LastDimension_MultiDimArray.js | Use of IndexRane for reading a range of indexes of a multi-dimentionsal array where the last 3 elements of the last dimension in the array are read for each data type. | FAILED | No MultiDimensionalArray items configured. Please check settings.
ReadArray_IndexRange_BoundsCheck_PartialReturn.js | IndexRange's lower bound is within the array's range but exceeding the array`s upper bound for each support array data type. | FAILED | Read. Response.
Read_Attributes_MultipleValidOneInvalid_ErrorForInvalid.js | Read: Multiple valid attributes and one invalid attribute, from a single valid node. | PASSED
Read_Attribute_FromInvalidNodeId.js | Read: Valid attribute from an invaild (non existent) node. | PASSED
Read_BrowseName_EmptyNodeId.js | Read: Valid attribute from a node id with invalid syntax: String Id: Empty/null | PASSED
ReadValidAttributeFromNodeIdWithEmptyStringId.js | Read: Valid attribute from a node id with invalid syntax: Byte Id: Empty/null | PASSED
ReadMultipleAttributes_MixedValidUnknownInvalidNodes.js | Read: Valid attributes (ids: 1, 3, 4, 5) from a set of nodes containing valid nodes, non-existent nodes, and nodes with invalid node id syntaxes | FAILED | Read. Response. Results[27] received 'BadNodeIdUnknown (0x80340000), but Expected: Good (0x00000000), when reading NodeId: ns=2;s=OPCDA_Connector_3~Channel1.
ReadValidAttributes_FromMultipleNonExistentNodes.js | Read: Valid attributes (ids: 1, 3, 4, 5) from multiple non-existent nodes | PASSED
ReadValidAttributes_FromNodesWithInvalidNodeIdSyntax.js | Read: Valid attributes (ids: 1, 3, 4, 5) from multiple nodes with invalid node id syntaxes | PASSED
ReadEmptyNodesArray.js | Read: NodesToRead array is empty. | PASSED
001.js | Write: Write a VQT, include VQ. | PASSED
002.js | Write: Write a VQT, include VQT (source). | PASSED
003.js | Write: Write a VQT, include VQT (both). | FAILED | Writing to SourceTimstamp+ServerTimestamp
004.js | Write: Write a VQT, include VT (source) only. | FAILED | The received SourceTimestamp (2025-05-28T01:14:17.
005.js | Write: Write a VQT, include V only. | PASSED
006.js | Write: Write a VQT, include VT (both) only. | FAILED | Writing to ServerTimestamp+SourceTimestamp+Value
007.js | Write: Write a VQT, include VQT (source) only. | PASSED
008.js | Write: Write a VQT, include VT (server) only. | FAILED | Writing to ServerTimestamp+Value
009.js | CreateMonitoredItems: Write StatusCode to Value (but not value) and call Publish. | FAILED | Did not expect a dataChange since the values written were the same, i.
010.js | CreateMonitoredItems: DataChangeFilter of VQT. | FAILED | Did not expect a dataChange since the values written were the same, i.
011.js | CreateMonitoredItems: Write VQT. | PASSED
Write_Value_Attribute_Multiple_Nodes.js | Write: Value attribute, multiple nodes. | PASSED
Write_AccessLevel_CurrentWrite_Expects_Good.js | Write: AccessLevel = CurrentWrite. Expects "Good". | PASSED
Write_Minimum_Value_For_Each_Supported_DataType.js | Write: Write the minimum value for each supported Data Type. | FAILED | Value written does not match the value the Server returned in a subsequent Read.
Write_Max_Value_Of_Each_Supported_DataType.js | Write: Max value of each supported data type. | FAILED | Value written does not match the value the Server returned in a subsequent Read.
Write_ByteString_To_Byte_Expects_Success.js | Write: ByteString to a Byte[]. Expects success. | FAILED | Byte[] node type not configured within the setting: /Server Test/NodeIds/Static/All Profiles/Arrays/Byte or not writable.
Write_LocalizedText_All_Some_No_Parameters_Of_Structure_Type.js | Write: LocalizedText; write to all, some, and no parameters of this structure type. | FAILED | LocalizedText not configured in setting: /Server Test/NodeIds/Static/All Profiles/Scalar/LocalizedText or not writable.
Write_Values_That_Are_Subtype_Of_UInteger.js | Write: Write values that are the 'subtype' of a UInteger. | FAILED | UInteger not configured or not writable, please check setting: /Server Test/NodeIds/Static/All Profiles/Scalar/UInteger.
Write_NaN_To_All_Floats.js | Write: NaN to to all floats. | FAILED | Node type(s) not configured within the setting: /Server Test/NodeIds/Static/All Profiles/Arrays/Float,/Server Test/NodeIds/Static/All Profiles/Arrays/Double.
Write_String_In_Extended_Codepage.js | Write string in extended codepage. | PASSED
Write_Value_Attribute_NoStatus_NoTime_Node_ValueRank_Array_Entire_Array.js | Write to the Value attribute (without statusCode, sourceTimestamp, or serverTimestamp) of nodes that has a ValueRank of an array. Write the entire array. | FAILED | No (writable) Array items configured. Please check settings.
Write_Value_Attribute_NoStatus_NoTime_Several_Nodes_ValueRank_Array_Entire_Array.js | Write to the Value attribute (without statusCode, sourceTimestamp, or serverTimestamp) of several nodes that has a ValueRank of array. Write the entire array. | FAILED | No (writable) Array items configured. Please check settings.
Write_Value_Attribute_NoStatus_NoTime_Node_ValueRank_MultiDimensional_Array_Entire_MultiDimensional_Array.js | Write to the Value attribute (without statusCode, sourceTimestamp, or serverTimestamp) of nodes which have a ValueRank of a multi-dimensional array. Write the entire multi-dimensional array. | FAILED | No MultiDimensionalArray items configured. Please check settings.
Write_Value_Attribute_NoStatus_NoTime_Several_Nodes_ValueRank_MultiDimensional_Array_Entire_MultiDimensional_Array.js | Write to the Value attribute (without statusCode, sourceTimestamp, or serverTimestamp) of several nodes which have aValueRank of a multi-dimensional array. Write the entire multi-dimensional array. | FAILED | No MultiDimensionalArray items configured. Please check settings.
Write_Empty_Nodes_To_WriteArray.js | Write: Empty nodesToWrite array. | PASSED
Write_To_Invalid_Attribute_Of_Invalid_Node.js | Write: Write to a valid attribute of an invalid Node. | PASSED
Write_Valid_Node_For_Node_Using_Invalid_Syntax.js | Write: Write to a valid node for a Node using an invalid syntax. | PASSED
Write_Invalid_Attribute.js | Write: Invalid attribute. | PASSED
Write_Invalid_Attribute_To_Valid_Node_Multiple_Times_In_Same_Call.js | Write: Invalid attribute to a valid node, multiple times in the same call. | PASSED
Write_To_Node_Whose_AccessLevel_Is_ReadOnly_Expect_Bad_NotWritable.js | Write: to a node whose AccessLevel is Read Only. Expect Bad_NotWritable. | FAILED | Setting not configured: '/Server Test/NodeIds/SecurityAccess/AccessLevel_CurrentRead_NotCurrentWrite'.
Write_Value_Using_Wrong_DataType.js | Write: Write a value using the wrong data-type. | FAILED | Write().Response.Results[0].StatusCode = 'Good (0x00000000)'; but StatusCode 'BadTypeMismatch (0x80740000)' was expected (Node Setting: '/Server Test/NodeIds/Static/All Profiles/Scalar/Bool') StatusCode expectations for this call were... [0] Expected: BadTypeMismatch (0x80740000)
Write_Null_To_Each_DataType.js | Write: Write a <null> to each data-type. | FAILED | Value written does not match the value the Server returned in a subsequent Read.
WriteInteger_Receives_Values_Of_Incorrect_SubType.js | Write: Integer receives values of incorrect sub-type. | FAILED | Integer data-type not configured or not writable, please check the setting: /Server Test/NodeIds/Static/All Profiles/Scalar/Integer.
WriteError_Write_LocalizedText_With_Non_Existent_Locale.js | Write: LocalizedText with non-existent Locale. | FAILED | LocalizedText not configured or not writable. Please check setting: /Server Test/NodeIds/Static/All Profiles/Scalar/LocalizedText.
Base Eventing | Some Events are optional features for an OPC UA Server. | FAILED | Not Implemented
Monitor Events | Support creation of MonitoredItems using a Notifier attribute | FAILED | Not Implemented
Base Information | Base Information. (optional) | FAILED | Current element (i=2274) is part of the server diagnostics object. The cached element is not existing anymore in the servers address space. Skipping the validation.
ServerObject.StructureConsistency.NamespaceMapping.js | Server node. | FAILED | Current element (i=2274) is part of the server diagnostics object. The cached element is not existing anymore in the servers address space. Skipping the validation.
CoreSystemNodes.BrowseName.Read.js | Read BrowseName of system-level nodes. | PASSED
Read_ServerDiagnostics_BrowseName.js | Read ServerDiagnostics BrowseName | PASSED
Check_CurrentSessionCount_And_CumulatedSessionCount.js | Check CurrentSessionCount and CumulatedSessionCount | PASSED
Check_SamplingIntervalDiagnosticsArray.js | Check SamplingIntervalDiagnosticsArray | PASSED
Check_SubscriptionDiagnosticsArray.js | Check SubscriptionDiagnosticsArray | PASSED
Check_SubscriptionDiagnosticsArray_In_Real_Time.js | Check SubscriptionDiagnosticsArray in real time | FAILED | Expected a value less than <1> but got <1>.
Verify_ModifyCount_Subscription_Diagnostic.js | Verify ModifyCount subscription diagnostic. | PASSED
Check_RepublishMessageCount_Subscription_Diagnostic.js | Check RepublishMessageCount subscription diagnostic | FAILED | Read. Response. Results (count: 23) with RequestHandle=44 StatusCodes check: [0] (Setting: '/Server Test/NodeIds/Static/All Profiles/Scalar/Bool') StatusCode is Good (0x00000000), .
Check_PublishRequestCount_And_DataChangeNotificationsCount_Subscription_Diagnostics.js | Check PublishRequestCount and DataChangeNotificationsCount subscription diagnostics | PASSED
Check_DisabledMonitoredItemCount_Diagnostics_Property.js | Check DisabledMonitoredItemCount diagnostics property | PASSED
Check_MonitoringQueueOverflowCount_Subscription_Diagnostic.js | Check MonitoringQueueOverflowCount subscription diagnostic | FAILED | MonitoringQueueOverflowCount should be zero because all monitored items should be active.
Check_Current_CumulatedSubscriptionCount.js | Check Current/CumulatedSubscriptionCount | PASSED
Repeat_Current_CumulatedSubscriptionCount.js | Repeat Current/CumulatedSubscriptionCount | PASSED
Check_ServerDiagnostics_EnabledFlag.js | Check ServerDiagnotics.EnabledFlag. | FAILED | Unable to write to the EnabledFlag node. Aborting test.
Verify_EnabledFlag_Toggle_DoesNot_Increase_SessionCount.js | Verify EnabledFlag toggle doesnt increase session count | FAILED | Unable to write to the EnabledFlag node. Aborting test.
Static_Diagnostics_Return_BadNotReadable_When_EnabledFlag_Is_False.js | Static diagnostics return BadNotReadable when EnabledFlag=false. | FAILED | Unable to write to the EnabledFlag node. Aborting test.
Test_Sessions_Are_Added_To_SessionsDiagnosticsSummary.js | Test sessions are added SessionsDiagnosticsSummary | PASSED
Check_Security_RejectedSessionCount.js | Check (Security-)RejectedSessionCount | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenInvalid (0x80200000) or BadIdentityTokenRejected (0x80210000) or BadUserAccessDenied (0x801f0000)
CreateSubscription_With_Zero_Items.js | CreateSubscription with 0 items. | PASSED
Two_Subscriptions_Both_Checked.js | 2 Subscriptions; both checked. | PASSED
Invalid_SubscriptionId.js | Invalid SubscriptionId | PASSED
Call_GetMonitoredItems_SubscriptionId_Belongs_To_Another_Session.js | Call GetMonitoredItems specifying SubscriptionId belonging to another session. | PASSED
Base Info OptionSet | The Server supports the VariableType OptionSet. | FAILED | Not Implemented
Validate_Correctness_Of_ResendData_Method.js | Validate the correctness of the ResendData method. | PASSED
Verify_DataChangeNotifications_Sent_AllMonitoredItems_MonitoringModeReporting.js | Verify DataChangeNotifications for all MonitoredItems of a Subscription are sent, when all MonitoredItems have the MonitoringMode Reporting. | FAILED | CreateMonitoredItems().
Verify_DataChangeNotifications_Sent_AllMonitoredItems_MonitoringModeReporting_PublishingIntervalNotTriggered.js | Verify DataChangeNotifications for all MonitoredItems of a Subscription are sent, when all MonitoredItems have the MonitoringMode Reporting but the PublishingInterval is not triggered yet. | FAILED | The ResendData method is available in the address space of the server returned BadNotImplemented when calling it. Please verify that this CU is optional in the desired target profile. Aborting Conformance Unit.
Verify_ServerCapabilities_Object.js | Verify ServerCapabilities object | PASSED
Check_MinSupportedSampleRate.js | MinSupportedSampleRate | FAILED | No node configured that can be used for this test case. A node without the MinimumSamplingInterval attribute set is required.
Check_MaxBrowseContinuationPoints.js | MaxBrowseContinuationPoints | PASSED
Check_MaxArrayLength.js | MaxArrayLength | FAILED | No writable Arrays configured in Settings. See settings > ServerTest > NodeIds > Static > All Profiles > Arrays
Check_MaxStringLength.js | MaxStringLength | WARNING
Check_MaxByteStringLength.js | MaxByteStringLength | FAILED | ByteString variable not configured in CTT settings.
Check_MaxNodesPerRead.js | MaxNodesPerRead | FAILED | MaxNodesPerRead is set to zero.
Check_MaxNodesPerWrite.js | MaxNodesPerWrite | FAILED | MaxNodesPerWrite is set to zero.
Check_MaxNodesPerMethodCall.js | MaxNodesPerMethodCall | FAILED | MaxNodesPerMethodCall is set to zero.
Check_MaxNodesPerBrowse.js | MaxNodesPerBrowse | FAILED | MaxNodesPerBrowse is set to zero.
Check_MaxNodesPerRegisterNodes.js | MaxNodesPerRegisterNodes | FAILED | MaxNodesPerRegisterNodes is set to zero.
CheckTypesFolderStructure.js | Level 1 folders exist | PASSED
DataTypesValidation.js | Walks through the DataTypes folder, in the TypeSystem, verifying compliance to UA Parts 3 and 5. | PASSED
EventTypesValidation.js | Walks through the EventTypes folder, in the TypeSystem, verifying compliance to UA Parts 3 and 5. | PASSED
ObjectTypesValidation.js | Walks through the ObjectTypes folder, in the TypeSystem, verifying compliance to UA Parts 3 and 5. | PASSED
ReferenceTypesValidation.js | Walks through the ReferenceTypes folder, in the TypeSystem, verifying compliance to UA Parts 3 and 5. | FAILED | IsAbstract=Y; Symmetric=Y; so inverseName should be unavailable, but it is.
VariableTypesValidation.js | Walks through the VariableTypes folder, in the TypeSystem, verifying compliance to UA Parts 3 and 5. | PASSED
001.js | Check ValueAsText property on ALL configured nodes | FAILED | No nodes with .ValueAsText property found. If your server has them then please make sure they are specified anywhere in the CTT settings.
Data Access | ConformanceUnits specific to Clients and Servers that deal with the representation and use of automation data as specified in Part 8 of the OPC UA specification. | FAILED | Unable to find a node of type AnalogItemType featuring an `InstrumentRange` property.
Data Access AnalogItemType | Support AnalogItemType Variables with corresponding Properties. | FAILED | Unable to find a node of type AnalogItemType featuring an `InstrumentRange` property.
000.js | Type is defined in the address-space. | PASSED
001.js | Read: Value attribute of an analog node of each of the following data type: Double, Float, Int16, UInt16, Int32, UInt32, Int64, UInt64. Perform each read separately. | FAILED | Read() returned a value that was not of the expected data-type. Expected <8> but got <6>.
002.js | Read: Value attribute of an analog node of each of the following data type: Double, Float, Int16, UInt16, Int32, UInt32, Int64, UInt64. Perform the reads in a single call. | FAILED | Read() returned a value that was not of the expected data-type. Expected <8> but got <6>.
003.js | Read: EURange property of an analog node. | FAILED | Test Aborted. Specified Node does not have an EURange property.
004.js | Read: EURange property of multiple analog nodes. | FAILED | Test Aborted. Specified Node does not have an EURange property.
005.js | Read: EURange property of an analog node. If the EURange exists, write values exceeding the lower bound and upper boound (i.e. lowerbound - 1/upperbound + 1 respectively) | FAILED | Response. Results[1].
006.js | Write: The following 3 values to an analog node (test each supported type): EURange.Low, EURange.High, and a number in the middle of the EURange. | FAILED | Test Aborted. Specified Node does not have an EURange property.
007.js | Write: No InstrumentRange; Write() the max value of datatype, min value of datatype, a value in the middle of the datatype range. | FAILED | Response. Results[1].
008.js | DeadbandAbsolute of 10. | FAILED | Results[0]. StatusCode is not Good Received: BadNoMatch (0x806f0000).
009.js | Write: To the EURange attribute. | FAILED | Specified node '/Server Test/NodeIds/Static/DA Profile/AnalogItemType/Double' does not have an EURange property.
010.js | Subscribe: Add monitored items of analog type (each supported datatype) to an enabled subscription. Wait for a publishing interval and call publish to verify the values received match the expected datatype of each node. | FAILED | DataType received for analog node '/Server Test/NodeIds/Static/DA Profile/AnalogItemType/Int64' does not match the expected type.
011.js | Subscribe: Add monitored items of analog type (each supported datatype) to an enabled subscription. Wait for a publishing interval and call publish to verify the values received match the expected datatype of each node. | FAILED | DataType received for monitored item '/Server Test/NodeIds/Static/DA Profile/AnalogItemType/Int64' does not match the expected type.
012.js | Subscribe: Add monitored item (configured with an EURange and a PercentDeadband filter value of 10) for each supported data-type to an enabled subscription. Call publish. Perform two writes to each item: 1) Will pass the deadband, 2) Will not pass the deadband. Call publish after each write. | FAILED | Unable to find a node of type AnalogItemType featuring an `InstrumentRange` property.
013.js | Analog Types: Should operate with TranslateBrowsePathsToNodeIds. | PASSED
014.js | Analog Types: Should operate with TranslateBrowsePathsToNodeIds (multiple Analog nodes). | PASSED
015.js | Browse: The available forward-references of an analog node. | FAILED | Static Analog
016.js | Browse: The available inverse-references of an analog node. | PASSED
017.js | Browse: The available references (both directions) of an analog node. | FAILED | Static Analog
018.js | Write to EngineeringUnits | FAILED | Unable to find a node of type AnalogItemType featuring an `EngineeringUnits` property.
019.js | Write a value equal to EURange.Low and then EURange.High. | FAILED | Results[0]. StatusCode is not Good Received: BadNoMatch (0x806f0000).
020.js | Write a value exceeding the InstrumentRange. | FAILED | Unable to find a node of type AnalogItemType featuring an `InstrumentRange` property, which is an OPTIONAL property.
021.js | TranslateBrowsePathToNodeIds requests InstrumentRange, EURange, and EngineeringUnits for all AnalogItems. | FAILED | Response. Results[1].
Err-001.js | Write: A complex structure (incorrect type) to an analog item. | FAILED | Write().Response.Results[0].StatusCode = 'Good (0x00000000)'; but StatusCode 'BadTypeMismatch (0x80740000)' was expected (Node Setting: '/Server Test/NodeIds/Static/DA Profile/AnalogItemType/Double') StatusCode expectations for this call were... [0] Expected: BadTypeMismatch (0x80740000)
Data Access ArrayItemType | Provide Variables of ArrayItemType or one of its subtypes (YArayItemType, XYArrayItemType, ImageArrayType, CubeArrayType, NDimensionArrayType). The actual subtypes that supported will be listed. Support for this type include supporting all of the mandatory properties including AxisInformation. | FAILED | Not Implemented
Data Access ComplexNumber | Supports the Complex Number data type. This data type is available for any variable types that do not have other explict restrictions. | FAILED | Not Implemented
Data Access DataItems | Provide Variables of DataItemType or one of its subtypes. Support the StatusCodes specified in the DataAccess part of the OPC UA specification. Support of optional Properties (e.g. "InstrumentRange") shall be verified during certification testing and will | FAILED | DataItem nodes not defined. Check settings: /Server Test/NodeIds/Static/DA Profile/DataItemType.
Data Access MultiState | Support MultiStateDiscreteType Variables with corresponding Properties. | FAILED | MultiStateValueDiscrete nodes not defined. Check settings: /Server Test/NodeIds/Static/DA Profile/MultiStateValueDiscreteType.
MultiStateDiscreteType_StructureValidation.js | Type is defined in the address-space. | PASSED
Write_To_SingleNode_ThisType_EachValue_SupportedByEnumerationLength.js | Write: to a Single node of this type, each value as supported by the enumeration length. | FAILED | Data Type of .
Data Access PercentDeadBand | Support PercentDeadband filter when monitoring AnalogItemType Variables. | FAILED | Test cannot be completed: 3 of 5 required AnalogItem nodes configured in settings.
Data Access Semantic Changes | Support Semantic changes of AnalogItemType items (EURange Property and/or EngineeringUnits Property). Support semantic change StatusCode bits where appropriate. | FAILED | Analog item '/Server Test/NodeIds/Static/DA Profile/AnalogItemType/Double' does not have an EngineeringUnits property which is legal because its an optional property.
Data Access TwoState | Support TwoStateDiscreteType Variables with corresponding Properties. | FAILED | TwoStateDiscreteType
History |  | FAILED | No historical items of type Array (2-dimensions) are configured in settings. Skipping test.
Security | Security related ConformanceUnits that can be profiled. | FAILED | Secure endpoint using Aes128-Sha256-RsaOaep not found!
Security Aes128-Sha256-RsaOaep | A suite of algorithms that uses SHA256 as Key-Wrap-algorithm and AES128-CBC for encryption algorithms. SymmetricSignatureAlgorithm Hmac-Sha2-256 (http://www.w3.org/2001/04/xmldsig-more#hmac-sha2-256) SymmetricEncryptionAlgorithm Aes128 (http://www.w3.org/2001/04/xmlenc#aes128-cbc | FAILED | Secure endpoint using Aes128-Sha256-RsaOaep not found!
Security Aes256-Sha256-RsaPss | A suite of algorithms that uses SHA256 as Key-Wrap-algorithm and AES256-CBC for encryption algorithms. SymmetricSignatureAlgorithm Hmac-Sha2-256 (http://www.w3.org/2001/04/xmldsig-more#hmac-sha2-256) SymmetricEncryptionAlgorithm Aes256 (http://www.w3.org/2001/04/xmlenc#aes256-cbc | FAILED | Secure endpoint using Aes256-Sha256-RsaPss not found!
Security Basic 128Rsa15 | A suite of algorithms that uses RSA15 as Key-Wrap-algorithm and 128-Bit for encryption algorithms. SymmetricSignatureAlgorithm HmacSha1 (http://www.w3.org/2000/09/xmldsig#hmac-sha1) SymmetricEncryptionAlgorithm Aes128 (http://www.w3.org/2001/04/xmlenc#a | FAILED | Secure endpoint using 128Rsa15 not found!
Security Basic 256 | A suite of algorithms that 256-Bit for encryption algorithms SymmetricSignatureAlgorithm HmacSha1 (http://www.w3.org/2000/09/xmldsig#hmac-sha1) SymmetricEncryptionAlgorithm Aes256 (http://www.w3.org/2001/04/xmlenc#aes256-cbc) AsymmetricSignatureAlgorit | FAILED | Secure endpoint using 256 not found! Aborting conformance-unit.
Security Basic 256Sha256 | A suite of algorithms that uses SHA256 as Key-Wrap-algorithm and 256-Bit for encryption algorithms. SymmetricSignatureAlgorithm HmacSha256 (http://www.w3.org/2001/04/xmldsig-more#rsa-sha256) SymmetricEncryptionAlgorithm Aes256 (http://www.w3.org/2001/04/xmlenc#sha256 | PASSED
Security Certificate Validation | Certificate will be validated as specified in OPC UA Part 4. This includes among others structure and signature examination. Allowing for some validation errors to be suppressed by administration directive. | FAILED | Current stack doesn't allow us to send an empty ClientCertificate, therefore we need to skip this test for now.
SecurityCertificateValidation:ActivateInsecureSessionValidateCertPerSpecification.js | Insecure channel. Activate a session. Validate certificate per specification. Expects successful connection and valid certificate. | PASSED
SecurityCertificateValidation:ConnectWithClientCertSignedByUntrustedButKnownCAWithoutRevocation.js | Connect using a client certificate signed by a not trusted but known CA where there is no revocation list available. | FAILED | DisableCertificateRevocationOverride is not set in the CTT Settings but the connection was granted by the server.
SecurityCertificateValidation:AttemptSecureSessionWithEmptyClientCertificate.js | Attempt a secure session and send an empty clientCertificate. | FAILED | Current stack doesn't allow us to send an empty ClientCertificate, therefore we need to skip this test for now.
SecurityCertificateValidation:SecureChannelUntrustedCertificateExpectsBadSecurityChecksFailed.js | Secure channel. Untrusted certificate. Expects BadSecurityChecksFailed. | FAILED | OpenSecureChannel. Response is not good; received 'Good (0x00000000)'.
SecurityCertificateValidation:SecureChannelExpiredCertificateExpectsGoodOrBadCertificateTimeInvalid.js | Secure channel. Expired certificate. Expects Good or BadCertificateTimeInvalid | FAILED | OpenSecureChannel. Response is not good; received 'BadSecurityChecksFailed (0x80130000)'.
SecurityCertificateValidation:SecureChannelNotYetValidCertificateExpectsGoodOrBadCertificateTimeInvalid.js | Secure channel. Not-yet-valid certificate. Expects Good or BadCertificateTimeInvalid. | FAILED | OpenSecureChannel. Response is not good; received 'BadSecurityChecksFailed (0x80130000)'.
SecurityCertificateValidation:SecureChannelIssuerUnknownExpectsBadSecurityChecksFailed.js | Secure channel. Issuer is unknown. Expects BadSecurityChecksFailed. | FAILED | OpenSecureChannel. Response is not good; received 'Good (0x00000000)'.
SecurityCertificateValidation:SecureChannelCertificateSignedWithWrongKeyExpectsBadSecurityChecksFailed.js | Secure channel. Certificate signed with wrong key. Expects BadSecurityChecksFailed. | PASSED
SecurityCertificateValidation:UsingInsecureConnectionSecurityNoneActivateSessionWhileSendingRevokedCertificate.js | Using an insecure connection (Security=None), activate a session while sending a certificate that has been revoked. | PASSED
SecurityCertificateValidation:AttemptSecureChannelAndSendACA.js | Attempt a secure Channel and send a CA certificate. | FAILED | DisableCertificateUseNotAllowed is not set in the CTT Settings but the connection was granted by the server.
SecurityCertificateValidation:SecureChannelIssuedCertificateExpectsGood.js | Secure channel. Issued certificate. Expects Good | PASSED
SecurityCertificateValidation:EncryptedChannelUsingRevokedCertificate.js | Encrypted channel using Revoked certificate | FAILED | DisableCertificateRevocationUnknown is not set in the CTT Settings but the connection was granted by the server.
SecurityCertificateValidation:ConnectUsingUntrustedIssuedCertOfCAWithNoRevocationList.js | Connect using an (trusted) issued certificate of a CA that has no revocation list available. | FAILED | DisableCertificateRevocationUnknown is not set in the CTT Settings but the connection was granted by the server.
SecurityCertificateValidation:ConnectUsingAnUntrustedIssuedCertOfCAWithNoRevocationListAvailable.js | Connect using an (untrusted) issued certificate of a CA that has no revocation list available. | FAILED | DisableCertificateRevocationUnknown is not set in the CTT Settings but the connection was granted by the server.
SecurityCertificateValidation:ConnectUsingAnUntrustedIssuedCertOfCAThatIsNotTrustedButAvailable.js | Connect using an (untrusted) issued certificate of a CA that is not trusted but available. | FAILED | OpenSecureChannel. Response is not good; received 'Good (0x00000000)'.
SecurityCertificateValidation:AttemptSecureChannelAndSendNotTrustedCertificateIssuedByUnknownCertificateAuthority.js | Attempt a secure channel and send a (not trusted) certificate that was issued by an unknown (not trusted) CertificateAuthority. | FAILED | OpenSecureChannel. Response is not good; received 'Good (0x00000000)'.
SecurityCertificateValidation:ConnectUsingARevokedCertificateThatIsNotTrusted.js | Connect using a Revoked certificate that is not trusted. | FAILED | The connection was granted by the server which is not allowed because the CA and the Application Instance Certificate are not trusted.
SecurityCertificateValidation:ConnectUsingATrustedClientCertificate.js | Connect using a trusted client certificate. | PASSED
SecurityCertificateValidation:ConnectUsingATrustedClientCertificate(sha1-1024).js | Connect using a trusted client certificate (sha1-1024). | FAILED | A secure channel is not available. This is only allowed for Nano and Micro Embedded Device Server Profiles.
SecurityCertificateValidation:ConnectUsingATrustedClientCertificate(sha1-2048).js | Connect using a trusted client certificate (sha1-2048). | FAILED | A secure channel is not available. This is only allowed for Nano and Micro Embedded Device Server Profiles.
SecurityCertificateValidation:ConnectUsingATrustedClientCertificate(sha2-2048).js | Connect using a trusted client certificate (sha2-2048). | PASSED
SecurityCertificateValidation:ConnectUsingATrustedClientCertificate(sha2-4096).js | Connect using a trusted client certificate (sha2-4096). | PASSED
Security None | A suite of algorithms that does NOT provide any security settings SymmetricSignatureAlgorithm - SymmetricEncryptionAlgorithm - AsymmetricSignatureAlgorithm - SymmetricKeyWrapAlgorithm - AsymmetricEncryptionAlgorithm - KeyDerivationAlgorithm PSha1 (h | PASSED
insecureChannelWithCertificatesAndNonce.js | Insecure channel. Provide certificates & nonce. Expects channel to open. | PASSED
insecureChannelWithNonceNoCertificates.js | Insecure channel. Provide nonce, no certificates. Expects channel to open. | PASSED
insecureChannelWithNonceOnly.js | Insecure channel. Provide Nonce, but no certificates. Expect channel to open. | PASSED
insecureChannelNoCertOrNonceExpectSecure.js | Insecure channel. Do not pass certificate or nonce. Expect secure channel to open. | PASSED
Security User Anonymous | The ability to accept or ignore application certificates. | FAILED | No endpoints found that do NOT support anonymous user identity token. All secure endpoints seem to allow for Anonymous. Aborting test.
Security User Name Password | User name password combination. Specific encryption of the password is required if no Message encryption is used. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenInvalid (0x80200000)
insecureChannelAuthSuccess.js | Insecure channel. Authenticate with success. | PASSED
secureChannelAuthSuccess.js | Secure channel. Authenticate with success. | PASSED
insecureChannelEmptyUserPassExpectTokenInvalid.js | Insecure channel; Empty username and password. Expect Bad_IdentityTokenInvalid. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenInvalid (0x80200000)
insecureChannelNonExistentUserExpectTokenRejected.js | Insecure channel. Non-existent user. Expecting Bad_IdentityTokenRejected. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000) or BadUserAccessDenied (0x801f0000)
insecureChannelValidUserEmptyPassNonceExpectGoodOrRejected.js | Insecure channel. Valid username, password empty (serverNonce added). Expected result, Good or Bad_IdentityTokenRejected. | PASSED
insecureChannelValidUserEmptyPassNoNonceExpectGoodOrRejected.js | Insecure channel. Valid username, password empty (serverNonce missing). Expected result, Good or Bad_IdentityTokenRejected. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000) or BadUserAccessDenied (0x801f0000)
insecureChannelWrongPasswordExpectTokenRejected.js | Insecure channel. Password is wrong. Expected Bad_IdentityTokenRejected. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000) or BadUserAccessDenied (0x801f0000)
insecureChannelUsernameDoesNotExistExpectTokenRejected.js | Insecure channel. Username doesnt exist. Expects Bad_IdentityTokenRejected. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000) or BadUserAccessDenied (0x801f0000)
insecureChannelPolicyIdMismatchExpectTokenInvalid.js | Insecure channel. policyId does not match server value. Expects Bad_IdentityTokenInvalid. | PASSED
insecureChannelEncryptionAlgorithmMismatchExpectTokenInvalid.js | Insecure channel. encryptionAlgorithm does not match server value. Expects Bad_IdentityTokenInvalid. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenInvalid (0x80200000)
secureChannelEmptyEncryptionAlgorithmExpectTokenInvalid.js | Secure channel. encryptionAlgorithm="". Expects Bad_IdentityTokenInvalid. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenInvalid (0x80200000)
insecureChannelValidUserNoAccessExpectAccessDenied.js | Insecure channel. Valid username/password; user has no access. Expects Bad_UserAccessDenied. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadUserAccessDenied (0x801f0000)
getEndpointsVerifyUniqueUserIdentificationPolicyId.js | Call GetEndpoints and verify that each provided PolicyId for UserIdentificationTokens is unique. | FAILED | The PolicyId: 2, is used for multiple UserIdentityTokens.
Security User X509 | A public/private key pair. Must be able to be adminstrativly disabled | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000)
validCertForValidConnection.js | Valid certificate for a valid connection | PASSED
validCertForNotTrustedUser.js | Valid certificate for not-trusted user. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000)
notYetValidCertTrusted.js | Not yet valid certificate; trusted | FAILED | DisableCertificateTimeInvalid is not set in the CTT Settings but the connection was granted by the server.
expiredX509Certificate.js | Expired certificate | FAILED | DisableCertificateTimeInvalid is not set in the CTT Settings but the connection was granted by the server.
revokedUserX509Cert.js | Revoked user X509 cert. | FAILED | DisableCertificateRevocationUnknown is not set in the CTT Settings but the connection was granted by the server.
applicationInstanceCertificateInstead.js | ApplicationInstanceCertificate instead. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenInvalid (0x80200000) or BadIdentityTokenRejected (0x80210000) or BadCertificateUseNotAllowed (0x80180000)
specifyDifferentPolicyId.js | Specify different PolicyId | PASSED
invalidUserCertificate.js | Invalid user certificate. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000)
validCertLocalCANotTrusted.js | Specify a valid certificate that has been issued by a local (i.e. not commercial CA like Verisign /Comodo etc.) certificate authority that is not trusted. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000)
validTrustedCertLocalCATrusted.js | Specify a valid certificate that has been issued by a local (i.e. not commercial CA like Verisign /Comodo etc.) certificate authority that is trusted. | PASSED
validTrustedCertLocalCANotTrustedButKnown.js | Specify a valid, trusted certificate that has been issued by a local (i.e. not commercial CA like Verisign /Comodo etc.) certificate authority that is not trusted but known. | PASSED
validNotTrustedCertLocalCANotTrustedButKnown.js | Specify a valid, not trusted certificate that has been issued by a local (i.e. not commercial CA like Verisign /Comodo etc.) certificate authority that is not trusted but known. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadIdentityTokenRejected (0x80210000)
notTrustedCertRevokedServerPolicyId.js | Specify a not trusted certificate that has been revoked, and a server-specified policyId. | FAILED | DisableCertificateRevocationUnknown is not set in the CTT Settings but the connection was granted by the server.
validTrustedUserCertEmptyUserIdentitySignature.js | Specify a valid/trusted user certificate and provide an empty UserIdentitySignature. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: BadSecurityChecksFailed (0x80130000); but Expected: BadUserSignatureInvalid (0x80570000) or BadIdentityTokenInvalid (0x80200000) or BadIdentityTokenRejected (0x80210000)
validTrustedUserCertInvalidUserIdentitySignature.js | Specify a valid/trusted user certificate and provide an invalid UserIdentitySignature. | PASSED
validTrustedUserCertUserIdentitySignatureInvalidAlgorithm.js | Specify a valid/trusted user certificate and provide an UserIdentitySignature created using an invalid Algorithm. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: BadSecurityChecksFailed (0x80130000); but Expected: BadUserSignatureInvalid (0x80570000) or BadIdentityTokenInvalid (0x80200000) or BadIdentityTokenRejected (0x80210000)
Session Services | An (OPC UA) Session is an application layer connection. | FAILED | Not enough locales supported by server. Need 2 or more; server supports 1; which contains: Size: 1 [0] = en-US
Session Base | Support the Session Service Set (CreateSession, ActivateSession, CloseSession) except the use of ActivateSession to change the Session user. This includes correct handling of all parameters that are provided. Note that for the CreateSession and Activa | FAILED | Not enough locales supported by server. Need 2 or more; server supports 1; which contains: Size: 1 [0] = en-US
001.js | CreateSession: RequestedSessionTimeout = 0; the RevisedSessionTimeout != 0. | PASSED
002.js | CreateSession: Create and Activate a session and stall the session to cause it to timeout. | PASSED
003.js | CreateSession: Server diagnostics shows an entry for the client session (if supported). | PASSED
004.js | ActivateSession: Default parameters. | PASSED
005.js | ActivateSession: Specify numerous LocaleIds in a ranked order. | FAILED | Not enough locales supported by server. Need 2 or more; server supports 1; which contains: Size: 1 [0] = en-US
008.js | ActivateSession: Call activateSession on a session that has been transferred to a different Channel. | PASSED
009.js | ActivateSession: Provide no software certificates. | PASSED
010.js | CloseSession: Default parameters. | PASSED
011.js | CloseSession: Call CloseSession 100x in a loop. | PASSED
012.js | Using SecurityPolicy None/anonymous, create a session while specifying a not-trusted certificate. | PASSED
013.js | No SessionName specified | PASSED
015.js | ActivateSession: Empty ClientSignature. | PASSED
Err-001.js | CreateSession: Create 2 Sessions. Use the same nonce twice! | PASSED
Err-004.js | CreateSession: Create the session but do not activate it before calling another service. | PASSED
Err-005.js | CreateSession: Invalid (too short) NonceId. | PASSED
Err-009.js | ActivateSession: Specify a UserIdentityToken type that is not supported. | FAILED | Cannot complete test. Kerberos token is the only unsupported UserIdentityToken and is currently not supported in the CTT!
Err-010.js | ActivateSession: Specify user login credentials that do not have sufficient privileges. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadUserAccessDenied (0x801f0000) or BadIdentityTokenRejected (0x80210000)
Err-013.js | CloseSession: Close an already-closed session. | PASSED
Err-014.js | CloseSession: Close a session that was never created. | PASSED
Err-019.js | In a loop, call CreateSession() until the maximum number of sessions is reached; call CreateSession once more. | WARNING
Err-022.js | Over a secure channel; call ActivateSession() specifying an empty ClientSignature. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: BadSecurityChecksFailed (0x80130000); but Expected: BadApplicationSignatureInvalid (0x80580000)
Err-023.js | Open an unsecure SecureChannel and create a Session using SecurityPolicy#None. | FAILED | This test case requires that the server does not provide an endpoint for SecurityPolicy#None. An unsecure endpoint has been found, therefore skipping this test case.
Session Cancel | Support the Cancel Service to cancel outstanding requests. | PASSED
001.js | Cancel: Default parameters. | PASSED
003.js | Cancel: Cancel a completed call. | PASSED
004.js | Cancel: Specify an invalid/non-existent RequestHandle. | PASSED
Session Change User | Support use of ActivateSession to change the Session user. | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadUserAccessDenied (0x801f0000)
001.js | Specify different user credentials when activating an already active session. Call Publish. | PASSED
002.js | Specify the same user credentials on a session that the user already owns, using the same channel. | PASSED
004.js | Change the owner of a session but specify invalid/incorrect credentials (e.g. good username, empty password). | FAILED | ActivateSession.Response.ResponseHeader.ServiceResult: Good (0x00000000); but Expected: BadUserAccessDenied (0x801f0000)
006.js | ActivateSession: Activate an already active session while specifying different user login credentials | PASSED
Session General Service Behaviour | Implement basic Service behaviour. This includes in particular: - checking the authentication token - returning the requestHandle in responses - returning available diagnostic information as requested with the 'returnDiagnostics' parameter - respe | PASSED
001.js | CreateSession: Default Parameters. | PASSED
002.js | CreateSession: SessionTimeout testing with RevisedSessionTimeout checking. | PASSED
003.js | CreateSession: RequestHeader.AuthenticationToken contains a valid NodeId. | PASSED
Session Minimum 1 | Support minimum 1 Session (total for all Clients). | PASSED
001.js | Create 2 sessions. | PASSED
Session Minimum 10 Parallel | Support minimum 10 parallel Sessions (total for all Clients). | PASSED
001.js | CreateSession: Creates 10 concurrent sessions. | PASSED
002.js | CreateSession: Create multiple (5) sessions each with the same Name. | PASSED
003.js | CreateSession: create more sessions than server can handle. | PASSED
Session Minimum 2 Parallel | Support minimum 2 parallel Sessions (total for all Clients). | PASSED
001.js | CreateSession: 2 sessions, activated and then closed. | PASSED
002.js | Create more sessions than the server supports. | PASSED
Session Minimum 50 Parallel | Support minimum 50 parallel Sessions (total for all Clients). | PASSED
001.js | CreateSession: Create 50 concurrent connections per CU "Session Minimum 50 Parallel" | PASSED
002.js | CreateSession: create more sessions than server can handle (attempts 60) | PASSED
Session Minimum 500 Parallel | Support minimum 500 parallel Sessions (total for all Clients). | FAILED | This conformance unit requires a minimum of 500 sessions. As only 10are configured the conformance unit is skipped.
View Services | Clients use the View Service Set to navigate through the AddressSpace or through a View as subset of the AddressSpace. | FAILED | [Configuration Issue?] Unable to conduct test. Check settings (node with references in both directions).
View Basic | Support the View Service Set (Browse, BrowseNext). | FAILED | [Configuration Issue?] Unable to conduct test. Check settings (node with references in both directions).
browseReferenceTypeIdNullAllReferences.js | Browse: ReferenceTypeId=<null> returns ALL references. | PASSED
browseReferencesForwardDirection.js | Browse: Should browse references in the forward direction. | FAILED | [Configuration Issue?] Unable to conduct test. Check settings (node with references in both directions).
browseReferencesInverseDirection.js | Browse: Should browse for references in the inverse direction. | FAILED | [Configuration Issue?] Unable to conduct test. Check settings (node with references in both directions).
browseReferencesSpecifiedRefTypeAndNOSubtypesMatch.js | Browse: Should return references of the specified ReferenceTypeId (without subtypes) when the ReferenceTypeId matches a reference. | PASSED
browseReferencesMatchingNodeClassMask.js | Browse: Should return references matching the node class as specified by the NodeClassMask. | PASSED
browseMultipleNodesInOneCall.js | Browse: Should browse multiple nodes in one call. | PASSED
browseMultipleNodesMixValidInvalidIds.js | Browse: Should browse multiple nodes with a mix of valid and invalid node IDs. | PASSED
browseAllReferencesNodeClassMaskZero.js | Browse: Should return all references when NodeClassMask is 0. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has Inverse And Forward References'.
browseReturnOnlyOneRefDescriptionField.js | Browse: Should return only the one Reference Description field specified by the ResultMask. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has Inverse And Forward References'.
browseReferencesSpecifiedRefTypeNoSubtypesParentMatch.js | Browse: Should return references of the specified ReferenceTypeId (without subtypes) when the ReferenceTypeId matches a parent of a reference. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has References of a ReferenceType and SubType'.
browseReferencesSpecifiedRefTypeSubtypesParentTypeMatch.js | Browse: Should return references of the specified ReferenceTypeId and its subtypes when the ReferenceTypeId matches the parent type of a reference. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has References of a ReferenceType and SubType'.
browseReferencesNodeClassView.js | Browse: Should return references of node class View. | FAILED | No Views available in the 'Views' folder. Skipping test.
browseNonNullRefViewFieldsExceptTypeDefinition.js | Browse: Should return non-null Reference Description fields for all node classes except Object and Variable. For Object and Variable, all fields should be non-null except TypeDefinition, which should be a null NodeId. | PASSED
browseReturnRefDescriptionFieldsByResultMask.js | Browse: Should return the Reference Description fields specified by the ResultMask. | FAILED | Reference nodes not defined. Check settings: /Server Test/NodeIds/References.
browseRefsRefTypeRecursiveSubtypeGrandparentMatch.js | Browse: Should return references of the specified ReferenceTypeId and its recursive subtypes when the ReferenceTypeId matches the grandparent type of a reference. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has References of a ReferenceType and SubType'.
browseReturnDiagnosticInfoByBitMask.js | Browse: Should return diagnostic info as specified by the returnDiagnostics bit mask. | PASSED
browseReturnDiagnosticsWhenZero.js | Browse: Should not return diagnostics when returnDiagnostics is 0. | PASSED
browseBadNodeIdUnknownNotInAddressSpace.js | Browse: Should return operation error Bad_NodeIdUnknown when the node to browse is not in the address space. | PASSED
browseBadBrowseDirectionInvalid.js | Browse: Should return operation result BadBrowseDirectionInvalid when the BrowseDirection is invalid. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has Inverse And Forward References'.
browseBadViewIdUnknownViewNotExists.js | Browse: Should return operation result BadViewIdUnknown when the View does not exist. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has Inverse And Forward References'.
browseBadReferenceTypeIdInvalid.js | Browse: Should return operation result Bad_ReferenceTypeIdInvalid when ReferenceTypeId does not exist. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has Inverse And Forward References'.
browseBadViewIdUnknownSpecifiedViewNotExists.js | Browse: Should return operation result Bad_ViewIdUnknown when the specified View does not exist. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting ''.
browseBadReferenceTypeIdNotRefTypeNode.js | Browse: Should return operation result Bad_ReferenceTypeIdInvalid when ReferenceTypeId is a node that is not a reference type. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has Inverse And Forward References'.
browseBadSecurityCheckFailedNullAuthToken.js | Browse: Should return service error Bad_SecurityChecksFailed when authenticationToken is null. | PASSED
browseBadSecurityCheckFailedAuthTokenNotExists.js | Browse: Should return Bad_SecurityChecksFailed when the authenticationToken does not exist. | PASSED
View Minimum Continuation Point 01 | Support minimum 1 continuation point per Session. | WARNING | [Configuration Issue?] Unable to conduct test. Check setting 'Has Inverse And Forward References'.
browseForMaximumOneReference.js | Browse: Should browse for a maximum of one reference. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting 'Has Inverse And Forward References'.
browseNextNextRefReleaseContinuationPoints.js | BrowseNext: Should browse for the next reference and release continuation points. | PASSED
browseNextReturnCPWhenReleaseFalseMoreRefs.js | BrowseNext: Should return a ContinuationPoint when ReleaseContinuationPoints is false and more references exist. | PASSED
browseNextToLastRefGoodEmptyCP.js | BrowseNext: Should browse through to the last reference at which point the operation result should have StatusCode Good and empty ContinuationPoint. | PASSED
browseReturnInverseRefsWhenDirectionInverse.js | BrowseNext: Should return Inverse references when the direction is Inverse. | FAILED | Unable to read setting: /Server Test/NodeIds/References/Has 3 Inverse References 1. This test needs a node that has at least 3 inverse references.
browseReturnRefsSpecifiedTypeNoSubtypes.js | BrowseNext: Should return references of the specified type when a ReferenceTypeId is specified and IncludeSubtypes is false. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has References of a ReferenceType and SubType'.
browseReturnRefsSpecifiedTypeWithSubtypes.js | BrowseNext: Should return references of the specified type and its subtypes when a ReferenceTypeId is specified and IncludeSubtypes is true. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting '/Server Test/NodeIds/References/Has References of a ReferenceType and SubType'.
browseNextReturnRefsMatchingNodeClassMask.js | BrowseNext: Should return references matching the specified NodeClassMask. | WARNING
browseNextReturnResultFieldsByResultMask.js | BrowseNext: Should return requested result fields as specified by the ResultMask. | PASSED
browseNextReturnFewerRefsRequestedOrRemaining.js | BrowseNext: Should return the number of references requested or the number remaining, whichever is fewer. | WARNING
browseNextReturnViewsWhenNodeClassMaskIncludes.js | BrowseNext: Should return Views when the NodeClassMask is set to include Views. | FAILED | Server does not have Views. This test will not be run.
browseNextReturnDiagnosticsByDiagnosticMask.js | BrowseNext: Should return requested diagnostics as specified by the diagnostic mask. | PASSED
browseNextNoDiagnosticInfoWhenMaskZero.js | BrowseNext: Should return no diagnostic info when the returnDiagnostics mask is 0. | PASSED
browseNextBadNoContinuationPointsMaxReached.js | Browse: Should return operation result Bad_NoContinuationPoints when no more continuation points can be allocated or the server's maximum has been reached. | FAILED | [Configuration Issue?] Unable to conduct test. Check setting 'Has Inverse And Forward References'.
browseNextBadContinuationPointInvalidPreviousSession.js | BrowseNext: Should return operation result Bad_ContinuationPointInvalid when using a ContinuationPoint used in a previous session. | PASSED
browseNextBadContinuationPointInvalidAfterRelease.js | BrowseNext: Should return operation result Bad_ContinuationPointInvalid after releasing the ContinuationPoint. | PASSED
browseNextBadContinuationPointInvalidAlreadyUsed.js | BrowseNext: Should return operation result Bad_ContinuationPointInvalid when the ContinuationPoint has already been used. | PASSED
browseNextBadSecurityCheckFailedNullAuthToken.js | BrowseNext: Should return service result Bad_SecurityChecksFailed when the AuthenticationToken is null. | PASSED
browseNextBadSecurityCheckFailedAuthTokenNotExists.js | BrowseNext: Should return service result Bad_SecurityChecksFailed when the AuthenticationToken does not exist. | PASSED
browseNextBadInvalidTimestampRequestHeader.js | BrowseNext: Should return service result Bad_InvalidTimestamp when RequestHeader.Timestamp is too far out of range. | PASSED
View Minimum Continuation Point 05 | Support minimum 5 continuation points per Session. This number has to be supported for at least half of the minimum required sessions. | FAILED | [Configuration Issue?] Cannot execute test. Settings not configured 'Has 3 Forward References 1, 2, 3, 4 and/or 5'.
browseReturnFiveContinuationPoints.js | Browse: Should return five continuation points. | PASSED
browseNextReturnMultipleContinuationPoints.js | BrowseNext: Should return multiple ContinuationPoints elements. | FAILED | [Configuration Issue?] Cannot execute test. Settings not configured 'Has 3 Forward References 1, 2, 3, 4 and/or 5'.
browseNextCombineRefsFromSeparateBrowseCalls.js | BrowseNext: Should return references for ContinuationPoints from separate Browse calls combined into one BrowseNext call. | FAILED | Setting(s) not configured. Please check '/Server Test/NodeIds/References/Has 3 Forward References 1' and '/Server Test/NodeIds/References/Has 3 Forward References 2'.
View Minimum Continuation Point 10 | Support minimum 10 continuation points per Session. This number has to be supported for at least half of the minimum required sessions. | FAILED | Not Implemented
View Minimum Continuation Point 50 | Support minimum 50 continuation points per Session. This number has to be supported for at least half of the minimum required sessions. | FAILED | Not Implemented
View RegisterNodes | Support the RegisterNodes and UnregisterNodes Services as a way to optimize access to repeatedly used Nodes in the Server's AddressSpace. | FAILED | The OperationLimit MaxNodesPerRegisterNodes is set to zero. OperationLimit was limited to 10000 for this test case. RegisterNodes succeeded and this test case cannot be validated.
NodesRegistration:VerifyReferenceToNodesToRegister[0].js | RegisterNodes: Should return a node that refers to NodesToRegister[0]. | PASSED
NodesRegistration:Verify5NodeReferences.js | RegisterNodes: Should return five nodes that refer to the five NodesToRegister. | PASSED
NodesRegistration:Verify25NodeReferences.js | RegisterNodes: Should return 25 nodes that refer to the 25 NodesToRegister. | PASSED
NodesRegistration:Verify50NodeReferences.js | RegisterNodes: Should return 50 nodes that refer to the 50 NodesToRegister. | PASSED
NodesRegistration:Verify100NodeReferences.js | RegisterNodes: RegisterNodes: Should return 100 nodes that refer to the 100 NodesToRegister. | PASSED
NodesRegistration:Verify20DuplicateNodeRegistrations.js | RegisterNodes: Should return 20 nodes when the same node is registered 20 times. | PASSED
NodesRegistration:VerifyMixedExistingandNon-ExistentNodeRegistrations.js | RegisterNodes: Should return five nodes when three existing and two non-existent nodes are registered. | PASSED
NodesRegistration:VerifyDiagnosticInfoBasedonBitmask.js | RegisterNodes: Should return diagnostic info as specified by the returnDiagnostics bit mask. | PASSED
NodesRegistration:VerifyNoDiagnosticInfoWhenBitmaskis0.js | RegisterNodes: Should not return diagnostics when returnDiagnostics is 0. | PASSED
NodesUnregistration:VerifySuccessfulSingleNodeUnregistration.js | UnregisterNodes: Should return Good service result when unregistering a registered node. | PASSED
NodesUnregistration:VerifySuccessful5NodeUnregistrations.js | UnregisterNodes: Should return Good service result when unregistering five registered nodes. | PASSED
NodesUnregistration:VerifySuccessful25NodeUnregistrations.js | UnregisterNodes: Should return Good service result when unregistering 25 registered nodes. | PASSED
NodesUnregistration:VerifySuccessful50NodeUnregistrations.js | UnregisterNodes: Should return Good service result when unregistering 50 registered nodes. | PASSED
NodesUnregistration:VerifySuccessful100NodeUnregistrations.js | UnregisterNodes: Should return Good service result when unregistering 100 registered nodes. | PASSED
NodesUnregistration:VerifySuccessfulMixedRegisteredandUnregisteredNodeUnregistrations.js | UnregisterNodes: Should return Good service result when unregistering three registered nodes and two unregistered nodes. | PASSED
NodesUnregistration:VerifySuccessfulMixedRegisteredandNon-ExistentNodeUnregistrations.js | UnregisterNodes: Should return Good service result when unregistering three registered nodes and two non-existent nodes. | PASSED
NodesUnregistration:VerifyNoUnregistrationWhenSourceNodeisUnregistered.js | UnregisterNodes: Should not unregister a registered node when the "source" node is unregistered. | PASSED
NodesUnregistration:VerifyDiagnosticInfoBasedonBitmask.js | UnregisterNodes: Should return diagnostic info as specified by the returnDiagnostics bit mask. | PASSED
NodesUnregistration:VerifyNoDiagnosticInfoWhenBitmaskis0.js | UnregisterNodes: Should not return diagnostics when returnDiagnostics is 0. | PASSED
NodesRegistration:HandleEmptyNodesToRegisterArray(Bad_NothingToDo).js | RegisterNodes: Should return Bad_NothingToDo when nodesToRegister[] is empty. | PASSED
NodesRegistration:HandleExcessiveNodeRequests.js | RegisterNodes: Should return Bad_OutOfMemory, Bad_EncodingLimitsExceeded or Bad_TooManyOperations when to many Nodes were requested. | FAILED | The OperationLimit MaxNodesPerRegisterNodes is set to zero. OperationLimit was limited to 10000 for this test case. RegisterNodes succeeded and this test case cannot be validated.
NodesRegistration:HandleNon-ExistentSingleNodeId(Bad_NodeIdUnknown).js | RegisterNodes: Should return the non-existent NodeId when the node does not exist. | PASSED
NodesRegistration:Error-InvalidSingleNodeId(Bad_NodeIdInvalid).js | RegisterNodes: specify invalid NodeId; expected Bad_NodeIdInvalid. | PASSED
NodesRegistration:Error-MixedValidandInvalidNodes(Bad_NodeIdInvalid).js | RegisterNodes: mix of valid and invalid nodes. Expects Bad_InvalidNodeId. | PASSED
NodesRegistration:Error-NullAuthenticationToken(Bad_SecurityChecksFailed).js | RegisterNodes: Should return service error Bad_SecurityChecksFailed when authenticationToken is null. | PASSED
NodesRegistration:Error-MissingAuthenticationToken(Bad_SecurityChecksFailed).js | RegisterNodes: Should return Bad_SecurityChecksFailed when the authenticationToken does not exist. | PASSED
NodesRegistration:Error-InvalidRequestTimestamp(Bad_InvalidTimestamp).js | RegisterNodes: Should return BadInvalidTimestamp when the RequestHeader.Timestamp is too far out of range. | PASSED
NodesRegistration:Error-NoNodestoUnregister(Bad_NothingToDo).js | UnregisterNodes: Should return Bad_NothingToDo when there are no nodes to unregister. | PASSED
NodesUnregistration:Error-NullAuthenticationToken(Bad_SecurityChecksFailed).js | UnregisterNodes: Should return service error Bad_SecurityChecksFailed when authenticationToken is null. | PASSED
NodesUnregistration:Error-MissingAuthenticationToken(Bad_SecurityChecksFailed).js | UnregisterNodes: Should return Bad_SecurityChecksFailed when the authenticationToken does not exist. | PASSED
NodesUnregistration:Error-InvalidRequestTimestamp(Bad_InvalidTimestamp).js | UnregisterNodes: Should return BadInvalidTimestamp when the RequestHeader.Timestamp is too far out of range. | PASSED
View TranslateBrowsePath | Support TranslateBrowsePathsToNodeIds Service. | FAILED | Test skipped because there are nodes required that are not configured in the settings. Review the log for more details.